## Site Requirements
Confidential
Items | Description | Requirement
Land Requirements | Total size of plot (Acres) | Min of 1,000 acres, up to 1,500 of buildable, contiguous land
| Preferred Dimensions (ft) | Square or rectangular preferred
| Topography | Flat or ability to level with limited terracing
| Zoning | Industrial - Must be able to accommodate semiconductor mfg; not within close proximity to any residental housing
| Access/Road Infrastructure | 4,000 – 6,000 vehicles per week accessing the service yard, 300 trucks per day - main concrete days 600, ~ 20 campus entry points
| Airport Proximity | Ability to connect to major airports with direct flights to Asia/Europe but NOT adjacaent to the property
| Climate concerns (weather) | No major weather risks and ability for employees to get into work even during local weather extremes
| Natural Disasters | Limited to no exposure to natural disasters
| Location | Within 30 minutes commute time to major metropolitan area
| Other | Minimal to no vibration, limited to no creeks/wetlands/preserves, no noise ordinance concerns, etc.
Building Requirement | # of planned fabs & support buildings | Initial Build: 1 Fab (2 mods), Central Utility Bldg., Bulk Gas Yard, Air Separation Unit, Electrical Sub Station, Office Bldg., Warehouse and Parking Full Build: 4 Fabs (8 mods), 4 CUBs, 4 BGYs, 4 ASUs, 4 ESSs, 4 Office Bldgs, 2 WHs & adequate parking
Utilities/ Infrastructure | Utility Supply Infrastructure | 100% redundant supply feeds & pipelines from 2 independent sources. Redundant major electric substation equipment, e.g., transformers, etc
| Power Availability - Estimated maximum of total annual electric power consumption (kwh) | Min: 300MVA Full Site Capability/Future Expansion Needs: 1200MVA
| Power Reliability/Quality | No voltage dips/surges outside F47 specs and no power outages/interuptions either planned or unplanned. no harmonics outside reasonable specs.
| Incoming Water - Depends on incoming quality and recycling strategy | Min: 3 MGD to 5 MGD, with consistent quality/constituents Full Site Capability/Future Expansion Needs: 12 MGD to 20 MGD
| Waste Water - Depending on recycle strategy | Min: 2.4 MGD to 4 MGD Full Site Capability/Future Expansion Needs: 9.6 MDG to 16 MGD
| Nitrogen - On Site Production of N2 with O2 being a by-product | Min: 3.1 MSCFH Full Site Capability/Future Expansion Needs: 12.4 MSCFH
| Natural Gas -Estimated maximum of natural gas consumption per hour (m3/h) | Min: 7000 m^3/hr, NG quality w/in specs Full Site Capability/Future Expansion Needs: 28,000 m^3/hr
| Haz Waste - Stored and trucked from Site | Min: 60,000 tons per year Full Site Capability/Future Expansion Needs: 240,000 tons per year
Operating hours | # of days/week the plant will be operational | 7 days
| Operating hours or number of shifts per day | 24 hours / 3 shifts
Construction | Construction Labor Skills and Availability | Evaluation of the availability / cost of construction labor / and the skills level of labor (productivity), Is it Right to work state or Union Driven State, State Semi /H-Tech construction projects. 3,000 - 4,000 contactors for Basebuild Phase
| Transportation Restriction | Evaluation of the Transportation of Large / heavy equipment to and from sites
| Local / State / Federal Law & Regulations | Evaluation of the understanding / stability of Laws and Regulation related to industry construction / contractors
| Permitting | Evaluation of the construction Permit process and overall requirements. Evaluation of the state seismic zones, prefered Zone 0-1.
Project Schedule | Land Acquisition Target Date | Q4 2021
| Construction Start Date | Q3 2023
| Operation Start Date | Q2 2026
| Date of Full Operation | TBD
Planned CAPEX | Total CAPEX Value - Excluding land and real estate | $20B initially and up to $80B
| CAPEX breakdown by year - tangible assets (such as machinery and equipment, excluding land) - $B | Y1: $1-2B, Y2: $3-4B, Y3: $5-6BM, Y4: $7-8B, Y5: $2-3B
Employment HC | Planned Total Headcount (Full Time Employees) | 3500+
| Headcount breakdown by educational level (employees with higher education and without higher education) | Engineers/Mfg. Techs/Other Support
| Headcount ramp up period and breakdown by year (to full operation) | Cumulative by Year Y1: 250, Y2:1,300, Y3: 3,000, Y4: 3,500
| Diverse & STEM Based | Local talent diversity in stem based education/experience
| Congingent Workers | Local talent diversity in stem based education/experience
| Construction Jobs | Trade availability to support 2mod construction SOC (3k-4k contractors)
Business Climate | Business environment | Pro business environment; history of tax breaks, regulatory streamlining and ongoing support for growing business
| Peer Company/Supplier Presence | Existing supply chain network in place or evidence of ability to attract key suppliers due to favorable business environment
| Economic Development Plan | Evidence of long-term plan to attract talent and investment
| Regulatory Processes | Well defined, stable and capable of fast track permitting; pro-business
Legal | Government & Legal System | Well developed contract law, well understood labor laws and levels of unionization, private property rights (including IP), reliable court system, foreign ownership of legal entities permitted
Security | Crime, Corruption, IP Protection, etc | Dependable police force, with reasonable response times for police and fire. Corruption is not endemic in business and government. Crime and violent crime rates should not be significantly above average. No recent terrorism targeting US interests or US private buiness. Govt. should not sponsor IP theft. Stable political system. Trustworthy contract security supplier must be available.
EHS/ Permitting | Soil & Groundwater Assessment | Deliver clean site to meet Company specifications. Company will conduct its own Phase I/II Environmental Property Assessment with written approval from current landowner(s).